Droop-Control DC Microgrid

Record of Changes

| Model | microgrid_florian.slx |
| --- | --- |
| Droop library | microgridLib.slx |
| System parameters | microgridParams.m |
| PV / boost parameters | SolarPVMPPTBoostData.mlx |
| Environment | MATLAB R2021b Update 8, Simscape Electrical (Specialized Power Systems) |

This document is written for someone who already knows the model. Part 4 lists every change block by block, in the order the blocks appear in the model, so a change can be traced straight to the diagram in front of you.

Reasoning that does not fit in a table cell is pulled out into numbered notes at the end. A → N7 in a table means "the argument is in Note 7". Several of the fixes were only reachable through attempts that failed first, and those attempts are recorded too — they are usually the part worth knowing.

# Contents

1   What changed, in brief	3

2   Running the project	5

3   Files added, and what each one is for	7

4   Changes, block by block	9

4.1   Model level	9

4.2   Top level	9

4.3   PV + Boost	12

4.4   Battery	12

4.5   Bidirectional DC/DC Converter	14

4.6   PCC + Grid	16

4.7   DROOP CONTROLLER	18

4.8   Supervisor (new)	20

4.9   Drain	22

4.10  DC Loads	22

4.11  microgridLib (new file)	23

5   Notes	24

6   Verification	30

7   Open items	33

# 1  What changed, in brief

## The architecture

The single biggest structural change is the grid path. Everything else is control layered on top of a plant that could not previously do what was asked of it.

|  | Before | After |
| --- | --- | --- |
| Grid path | 25 kV → transformer → diode rectifier → one-quadrant buck, duty wired to a constant 0.5 → bus. Import only, open loop. | 25 kV → breaker → transformer → line reactor → IGBT active front end → 1600 V DC link → half-bridge DC/DC → bus. Bidirectional, closed loop. |
| Battery converter | one device gated at a time by sign(Ibat_ref); outer loop a stiff 800 V PI | complementary switching with Vbat/Vbus feed-forward; outer loop is a droop node |
| PV | MPPT only; the constant-voltage branch was unreachable | automatic MPPT ↔ voltage-control handover at 850 V |
| Coordination between sources | none — the battery carried everything | a droop layer (one reusable library block, two instances) plus a supervisor that sets policy through it |
| Modes | grid-connected only | grid-connected, islanded, and reconnection with a resynchronisation window |
| Response to overload | the bus collapses | load shedding in four hysteretic stages |

## The major changes, in one list

- The grid path was rebuilt so power can flow both ways, and the transformer secondary was changed from grounded to ungrounded wye — without that the DC link collapsed in 5 ms every time. → N2

- The battery pack was resized and re-chemistried, from 250 V lead-acid to 400 V / 600 Ah lithium-ion, because the original could not carry the park on its own once the grid was disconnected. → N4

- A droop layer replaced the per-converter outer voltage loops, built as a real Simulink library block so both converters share one definition. → N9

- A supervisor was added that expresses the SOC and islanding policy through the droop layer — it moves set-points and clamps limits, and never writes a duty cycle. → N9

- The DC bus capacitor grew from 4.7 mF to 50 mF, because with proportional droop the bus capacitance and the droop band together fix the loop bandwidth. → N7

- Three measurement filters that started at zero were initialised at the operating point. Each one had been telling its controller the plant was dead for the first milliseconds of every run. → N8

- The grid converter is now gated off when islanded, not merely un-commanded — otherwise it drains its own DC link and the bus discharges into it. → N11

- The dump resistor became a backstop instead of a control: hysteresis relay, correctly sized resistor, and a threshold above the PV curtailment point so the PV backs off first. → N15

## Result

The same scenario — four 50 kW charging bays arriving in sequence — measured before and after:

|  | Before | After |
| --- | --- | --- |
| Bus voltage range | 660 – 840 V, oscillating | 764 – 799 V |
| Response to a 50 kW step | falls to 720 V | steps down onto the droop line |
| Dump resistor | chattering at 13.8 kA | never fires |
| Load sharing | battery carries everything | by policy, per mode and state of charge |
| Grid disconnected | not possible | bus held at 787 V; 5 V dip at the transition |
| Grid restored | not possible | reconnects with the loops reset; bus 786 – 793 V |
| Demand beyond the sources | bus collapses | bays shed in priority order, bus holds at 782 V |

# 2  Running the project

- Open MATLAB R2021b and set the Current Folder to the project folder. This matters — the model finds its data files relative to itself.

- Open microgrid_florian.slx. The Command Window must print: microgrid_florian: parameters loaded (SolarPVMPPTBoostData + microgridParams). If it does not, stop; nothing else will be meaningful.

- Press Run. Nothing else needs setting up — the stop time is already 1 s.

- Wait about 35 minutes. One second of model time costs roughly half an hour of wall clock. MATLAB will look frozen; it is not.

- Open MASTER SCOPE for the results. Everything is also in the base workspace as plain variables — Vdc, ILbat, Ibat_ref, Igrid, Vlink, SOC, island, shedLevel and the rest.

On the default scenario the four bays arrive between 0.25 and 0.55 s, the grid breaker opens at 0.70 s, recloses at 0.82 s, and the converter is released at 0.87 s.

## Check before you wait

Both of these run in seconds and catch most mistakes without a full simulation:

microgridCheck         % 64 structural checks + the threshold sweep

microgridCheck('results')    % 36 checks on a run that has already finished

## If the parameter load fails oddly

An error such as Undefined function 'mtimes' for input arguments of type 'cell' pointing at the PLL almost always means a stray base-workspace variable is shadowing a MATLAB built-in. The error points somewhere unrelated to the cause. Run clear, then reopen the model.

## Changing the scenario

Everything is in microgridParams.m. Edit, save, then reopen the model so it reloads.

| To do this | Change |
| --- | --- |
| Stay grid-connected for the whole run | mg.t_island = 10 — past the stop time. Not inf; the breaker and the step block both need a finite time. |
| Move the islanding or reconnection | mg.t_island, mg.t_reconnect, mg.t_resync |
| Start at a different state of charge | mg.SOC0 |
| Change the charging sessions | mg.evSessions — arrival, taper and departure per bay |
| Brighter or darker day | the Solar Irradiance W/m2 gain in PV + Boost/Irradiance (currently 150) |
| Retune any threshold or limit | the corresponding mg.* field — no block edits needed |

## The three scenarios

These reach behaviour a single default run cannot. Each starts the simulation in the background, so MATLAB returns immediately; poll get_param('microgrid_florian','SimulationStatus') and call microgridScenario('check') once it reads stopped. The scenario name is remembered, so you do not have to give it again.

microgridScenario('list')          % what is available

microgridScenario('soc90')         % battery above 80 % - supplies before the grid

microgridScenario('pvcurtail')     % battery full, PV in surplus - PV holds the bus

microgridScenario('overload')      % demand beyond the pack - bays are shed

microgridScenario('check')         % judge whichever scenario last ran

microgridScenario('restore')       % ALWAYS run this afterwards

microgridScenario('restore') puts every knob back. Skip it and your next run silently uses the scenario's settings.

# 3  Files added, and what each one is for

The model itself is unchanged in name and location. Everything below is new.

## Needed to open and run the model

| File | What it does | Why it exists |
| --- | --- | --- |
| microgridParams.m | Defines every system-level parameter in one struct, mg. Run automatically when the model opens. | Every value used to be a literal buried in a block — 810 V in a Constant, 0.5 in a Gain, 0.1 Ω in a branch. Nothing could be swept and nothing explained itself. |
| microgridLib.slx | A Simulink library holding DC Droop Node and Droop Reference. The battery and grid instances are linked, not copied. | Makes the droop controller one definition rather than two lookalike subsystems — editing the library updates both converters at once. |
| evLoadProfile.m | Generates the charging-bay resistance profiles from session descriptions in mg.evSessions. | A bay is now described the way a bay behaves — arrive, charge, taper, unplug — rather than as a matrix someone typed. |

## Verification

| File | What it does | Cost |
| --- | --- | --- |
| microgridCheck | 64 structural and configuration checks — block parameters, wiring, tags, limits, solver settings — then a sweep of every supervisor threshold. Closes and reopens the model first so the load callback is genuinely exercised from cold. | seconds |
| microgridCheck('thresholds') | The sweep on its own: lifts the Supervisor into a harness and drives every threshold in both directions, SOC 0 → 100 → 0 % and the bus 800 → 700 → 860 V. | 4 s |
| microgridCheck('results') | 36 checks on the logged signals of a completed simulation. This is what to run after pressing Run on the model. | after a run |
| microgridCheck('all') | The structural checks and the sweep, then a full simulation and a check of what it produced. | ~35 min |
| microgridScenario | Sets up the three operating cases a normal run cannot reach, judges the result, and restores every knob afterwards. | per scenario |

# 4  Changes, block by block

In the order the blocks appear in the model. Blocks not listed were not touched.

## 4.1  Model level — `microgrid_florian`

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| PreLoadFcn | none — empty model workspace | loads SolarPVMPPTBoostData then microgridParams | The model referenced eleven workspace variables and two variant objects that nothing loaded. Opening it on a clean MATLAB and pressing Run simply failed. |
| powergui frequency | 60 Hz | 50 Hz | The three-phase source is 50 Hz. Affects powergui's FFT and steady-state tools. |
| Solver MaxStep | 0.1 | auto (resolves to 5e-6) | A 0.1 s ceiling is meaningless beside a plant sampled at 5 µs. |
| Solver AbsTol | 1e-6 | auto | Let Simulink scale tolerance per state. |
| ZeroCrossAlgorithm | Nonadaptive | Adaptive | Added late; without it the PV boost's ideal IGBT chatters and aborts the run. → N16 |
| Solver type | ode23tb, variable-step | unchanged | Implicit (TR-BDF2), which is correct for a Simscape network coupled to a discrete SPS plant. Deliberately left alone. |
| StopTime | 1 s | unchanged |  |

## 4.2  Top level

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| Subsystem (legacy AC measurement panel) | active; 41 of its From tags had no matching Goto | Commented out | It was silently computing zeros, not failing. Commented rather than deleted so the work is preserved and it is reversible with one click. → N1 |
| From9, From10 (tag A) | fed MASTER SCOPE inputs 9 and 10 | deleted | The only signal the model consumed from the legacy panel; both destinations were already dead ends. |
| Subsystem1/LPF vq6 | 10 ms low-pass, Initialize off | Initialize on, Vdc_Init = mg.Vbus_nom | The droop reference ramped from 0 to 800 V over the first 50 ms of every run. → N8 |
| Voltage-Current Simscape Interface | v0 = 0 | v0 = mg.Vbus_nom, i0 = 0 | At t = 0 the whole SPS network saw 0 V while every capacitor sat at 800 V — a 16 kA first-sample spike. → N8 |
| Vpv_ctrl_ref (Constant) | — | new, mg.Vpv_ctrl_ref = 850 V | The PV curtailment target needs to be independent of the bus nominal. → N15 |
| From V0bat | — | new, feeds the battery converter's set-point inport | The battery droop set-point now comes from the Supervisor rather than the fixed Vdc_ref constant. |
| Supervisor | — | new subsystem — see §4.8 | Holds the whole SOC, islanding, curtailment and shedding policy. |
| Shed DC Load*, Open DC Load*, From shed* | — | new, twelve blocks | Load shedding — see §4.10. |

### MASTER SCOPE

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| Bus Voltage8, Bus Voltage9 | inports fed by tag A, wired to nothing inside | deleted | Dead channels — they displayed nothing. |
| Channel 7 | "PID Drain", From tag pid | "Drain ON", From tag Drain_ON | The signal is now a relay state, not a PI controller output. |
| Live channels | 10 (2 dead) | 8, all live | Bus voltage, load / battery / PV current, grid in and out, drain state, SOC. |

## 4.3  `PV + Boost`

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| Knob1 (dashboard) | bound to a block that does not exist in this model | deleted | Raised an error on every model update. A leftover from the original MathWorks example, where it controlled a load resistor since replaced by the four charging bays. |
| Slider Switch (dashboard) | manual MPPT / voltage-control selector | deleted | The handover is now automatic, and a hand switch on an automatic overvoltage protection is a way to defeat it. |
| Boost Converter/DC Bus Capacitor | 4.7 mF | `mg.Cbus` = 50 mF | This block physically is the bus capacitor. With proportional droop the capacitance sets the loop bandwidth. → N7 |
| PV Control/PV Mode/PV Mode | Constant, hard-wired to 1 (MPPT forever) | `From pvMode` | The constant-voltage branch was unreachable. It drives the selector port of both mode switches. |
| PV Control/Vref (inport) | fed from the top-level Vdc_ref = 800 V | fed from Vpv_ctrl_ref = 850 V | The specification wants the PV to hold ~850 V when it curtails, not the bus nominal. → N15 |
| Constant Voltage/Constant | divide-by-zero guard on the bus nominal | on mg.Vpv_ctrl_ref | Moved onto the same reference. |
| log pvEnMPPT, log pvEnVctrl | — | new To Workspace taps | So the handover can be checked after a run. |
| Constant-voltage branch itself | — | unchanged | It was already complete and already regulating the boost output (the DC bus) to its reference. Only the mode selector needed changing. |

## 4.4  `Battery`

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| Chemistry | Lead-Acid | Lithium-Ion | A 0.3C chemistry was being asked for 2C. Charging-park buffers are lithium-ion. → N4 |
| Nominal voltage | 250 V | 400 V | Halves the current for the same power, which is what the island duty needs. → N4 |
| Rated capacity | 2000 Ah (500 kWh) → 400 Ah | 600 Ah (240 kWh) | First reduced as disproportionate to a 200 kW park, then raised again once the battery had to carry that park alone. → N4 |
| Block nominal discharge current | 124 A (0.31C) | 543 A (0.90C) | Derived by the block from the two values above. |
| SOC | 30 % | mg.SOC0 (still 30 %) | Parameterised so it can be swept. |

## 4.5  `Bidirectional DC/DC Converter`

### Power stage

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| Inductor | 0.1 mH, R = 1 Ω | mg.Lbat = 0.5 mH, mg.Rbat_L = 5 mΩ | That 1 Ω was the only thing limiting the battery current, and the loop gains had effectively been tuned around it. → N6 |
| Battery-side capacitor | 1 mF, V₀ = 192 V | mg.Cbat, V₀ = mg.Vbat_C0 | Initial voltage now matches the pack. |
| Bus-side capacitor | 1200 µF, V₀ = 800 V | mg.Cbat_bus, V₀ = mg.Vbus_nom | Parameterised. |
| Devices | literals (Ron 1e-3, Rs 1e5) | mg.Ron, mg.Rsnub, mg.Csnub | Parameterised. |
| PWM Generator2 | stale instance, triangular carrier 0 → 1 | fresh library instance, −1 → +1 | The modulating signal sat below the carrier permanently: S1 latched on, S2 off, and the battery current ran away to 16 kA. → N5 |

### `Battery Converter Control`

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| Sign, Compare To Constant, Compare To Constant1, Product, Product1 | gated one IGBT at a time by sign(Ibat_ref) | all deleted | The duty-to-current gain changes sign between charge and discharge, so one PI cannot be right in both; and sign() chatters at zero current, which is where a droop-controlled battery lives. |
| S1 / S2 gating | one device switching, the other freewheeling | complementary, from the two PWM outputs | One continuous plant, one sign, no mode boundary at zero current — and genuinely bidirectional. |
| D ff, Sat Vbat, Sat Vbus, Sum D, Sat D, x2 D, one, Sum m | — | new — duty feed-forward chain | D = Vbat/Vbus − PI(Ibat_ref − ILbat). The current loop now only trims around the duty the converter actually needs. Saturation guards stop the first solver sample producing a nonsense ratio. |
| PI 2 (current loop) | unbounded integrator, then a clip | LimitOutput matching its saturation; gains mg.Kp_i_bat / mg.Ki_i_bat | Clamping anti-windup. Gains re-derived by internal model control against the real inductor. |
| PI 1 (outer bus-voltage loop) | stiff 800 V regulator | deleted | Replaced by a droop node. The converter is no longer a voltage regulator. |
| Battery Droop | — | new — linked instance of microgridLib/DC Droop Node | Slope mg.Rdroop_bat, limits ±mg.Ibat_max, filter mg.Tf_droop, filter IC mg.Vbus_nom. |
| Ibat limit + From Ibat_hi / From Ibat_lo | — | new — Saturation Dynamic on the droop node output | The Supervisor's policy limits, applied outside the library block rather than inside it. → N10 |
| Vdc_Ref (inport 1) | fed by the top-level Vdc_ref constant | fed by From V0bat | The set-point is now a live signal the Supervisor can bias. |

## 4.6  `PCC + Grid`

### Power stage — removed

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| Buck Converter | SPS averaged buck, duty wired to a Constant 0.5 | deleted | One-quadrant, open loop, and 0.5 × 1080 V = 540 V could never have reached an 800 V bus. |
| 0.5 and 0 Constants | the fixed duty and its companion | deleted | Superseded by a real control loop. |
| Three RLC branches, old current measurement | — | deleted | Belonged to the old chain. |
| Duty term | placeholder Terminator | deleted | The droop controller's duty output is now genuinely connected. |

### Power stage — changed and added

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| Universal Bridge | Device = Diodes | Device = IGBT / Diodes | Same block, now controllable, so the grid side can invert as well as rectify. |
| Transformer Winding2Connection | Yg (grounded wye) | Y (ungrounded wye) | The single fault that broke everything: a zero-sequence path collapsed the DC link in 5 ms. → N2 |
| Grid Breaker | — | new Three-Phase Breaker, closed, SwitchTimes = [mg.t_island mg.t_reconnect] | Islanding as a plant event rather than a control-level pretence. Shares its timing with the Supervisor so the two cannot disagree. |
| VI meas | — | new three-phase V-I measurement | Between transformer and reactor; positive current = grid → converter. |
| Line Reactor | — | new, mg.Lgrid / mg.Rgrid | ≈0.1 pu on the converter base. |
| Clink | — | new, mg.Clink = 4.7 mF, V₀ = mg.Vlink_ref = 1600 V | A 2-level VSC is a boost rectifier; its link must exceed the AC peak. → N3 |
| S_hi, S_lo | — | new IGBT/Diode half-bridge | Two-quadrant DC/DC from the 1600 V link to the 800 V bus. |
| Lgdc, Cbus | — | new output filter | Cbus is an RC branch — a pure C in parallel with the interface's ideal source is rejected by Simscape. |
| I grid, Vlink meas, Vbus meas | — | new instrumentation | For the scope channel and the control loops. |
| Gate block AFE, Gate block S_hi, Gate block S_lo, From gridEnable | — | new — all three gate paths multiplied by gridEnable | Clamping the current limits stops the converter being commanded; only gating stops it switching. → N11 |

### `Grid Converter Control` — new subsystem

Voltage-oriented control for the active front end, plus the duty path for the DC/DC. Gains are derived, not guessed: the inner loop by internal model control at one tenth the switching frequency, the outer loop against the link capacitor.

outer :  id_ref = PI( Vlink_ref - Vlink ) , limited to +/- Id_max

iq_ref = 0                                (unity power factor)

inner :  ud = vd + wL*iq - PI(id_ref - id)

uq = vq - wL*id - PI(iq_ref - iq)

m_abc = 2*dq0->abc(ud, uq, 0) / Vlink , saturated +/-1  ->  6 pulses

DC/DC :  D = Vbus/Vlink  +  ( D_droop - Dgdc_nom ) , saturated  ->  S_hi / S_lo

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| PI Vlink, PI id, PI iq | — (subsystem is new) | ExternalReset = level, driven by From afeReset | A loop that spent the island winding up against a dead grid must not be handed back a live one. → N12 |
| z0 V, z0 I | zero-sequence outputs left dangling | Terminators added | Found by the regression suite — the dq0 transforms' third outputs, which the control deliberately does not use. |
| Vbus/Vlink feed-forward | — | part of the new duty path | The DC/DC works into a stiff bus, so a 1 % duty error is thousands of amps. Feeding forward the ratio puts it at its operating point from t = 0. |

## 4.7  `DROOP CONTROLLER`

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| R_droop, Subtract, Subtract2, PID Controller1 | the outer voltage loop | deleted | Replaced by a droop node. |
| Grid Droop | — | new — linked instance of microgridLib/DC Droop Node | Slope mg.Rdroop_grid, limits mg.Igrid_min … mg.Igrid_max, filter IC mg.Vbus_nom. |
| Igrid limit + From Igrid_hi / From Igrid_lo | — | new — Saturation Dynamic on the droop node output | Policy limits, outside the library block. → N10 |
| From (set-point) | tag Vdc_ref | tag `V0grid` | Set-point now comes from the Supervisor. |
| Export limit | [0, Igrid_max] — import only | [mg.Igrid_min, mg.Igrid_max] | The hardware could already export; the controller was the thing blocking it. |
| PID Controller (inner current loop) | placeholder gains | IC = mg.Dgdc_nom, gains mg.Kp_i_gdc / mg.Ki_i_gdc | Derived from the real inductor; integrator starts at the operating duty rather than zero. |

## 4.8  `Supervisor` — new subsystem

The droop layer decides how the sources share. The Supervisor decides who is allowed to — and it does so without ever taking the decision away from the droop law. It is built entirely from ordinary Simulink blocks, no MATLAB Function and no Stateflow, so the whole policy can be read off the diagram. → N9

### Signals it publishes

| Added | What it does |
| --- | --- |
| V0bat | Battery droop set-point, biased by the SOC error: sat(Vbus_nom − k_soc·(SOC_target − SOC), 790, 810). Below target the battery sits on a lower droop line and absorbs; above target it sits higher and supplies before the grid. |
| Ibat_hi | Battery discharge limit. Zero below the SOC target while grid-connected — so the battery physically cannot discharge and the deficit comes from the grid. |
| Ibat_lo | Battery charge limit. Zero only at a full pack; there is deliberately no target-SOC ceiling on charging. |
| V0grid | Grid droop set-point, mg.V0_grid. |
| Igrid_hi, Igrid_lo | Grid import and export limits. Both zero while the converter is stood down. |
| gridEnable | May the grid converter switch at all. 1 − step(t_island) + step(t_release). |
| afeReset | Holds the three grid-converter integrators in reset — high for exactly as long as gridEnable is low. |
| pvMode | 1 = MPPT, 0 = PV voltage control. Latching hysteresis, 850 V on / 840 V off. |
| island | Is the breaker open. step(t_island) − step(t_reconnect). |
| shed1 … shed4 | Which charging bays are dropped. |

### Internals worth knowing

| Added | What it does |
| --- | --- |
| Bus filter (Vbus raw → Vbus) | A first-order lag built from an integrator, initialised at mg.Vbus_nom. Two reasons: a mode must not flip on switching ripple, and without a state in the Vbus → mode → duty → plant → Vbus path Simulink sees an algebraic loop and refuses to compile. → N8 |
| Slow bus filter (Vbus slow) | A second, much slower lag (mg.Tf_reshed = 50 ms) used only by load shedding, so shedding is decided on the fast bus and restoration on the slow one. → N13 |
| Nine Relay blocks | Every threshold in the model, each with its own hysteresis. There is no bare inequality anywhere — a bare comparison on a rippled signal chatters, and a chattering mode selector is worse than none. |
| Island, Reclose, Release steps | The three events of a full disconnect-and-return cycle. → N12 |

### Every threshold

| Threshold | Acts on | On | Off |
| --- | --- | --- | --- |
| Battery above target | SOC | 81 % | 79 % |
| Battery above floor | SOC | 17 % | 15 % |
| Battery full | SOC | 100 % | 98 % |
| Bus emergency (discharge override) | bus voltage | 770 V | 780 V |
| PV curtailment | bus voltage | 850 V | 840 V |
| Shed bay 4 / 3 / 2 / 1 | bus voltage | 755 / 745 / 735 / 725 V | 790 / 785 / 780 / 775 V |

Discharging is allowed when the microgrid is islanded, or SOC is above target, or the bus has fallen below 770 V — and in every case only while SOC is above the 15 % floor, which nothing overrides.

## 4.9  `Drain`

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| Trip threshold | 810 V, hard-coded | mg.Vdrain_on = 870 V | Must sit above the PV curtailment point, or the resistor burns energy the PV could simply stop generating. → N15 |
| Release threshold | none | mg.Vdrain_off = 845 V | Hysteresis. |
| Gate logic | a PI controller output fed into an ideal switch gate as a continuous value | Relay — a hysteresis comparator, 0/1 output | A switch gate is a binary input; a PI output is not. |
| Resistor | 0.1 Ω — 8.1 kA / 6.5 MW at 810 V | mg.Rdrain = Vdrain_on² / 200 kW ≈ 3.78 Ω | Sized to absorb the park's rated output, not to short the bus. |
| Switch Ron | 0.001 | mg.Rdrain_on | Parameterised. |
| Goto tag | pid | `Drain_ON` | The signal is a state now, not a PI output. |
| Transfer Fcn output | dangling line | Terminator added | Found by scanning every port, not by eye. |

## 4.10  `DC Load`, `DC Load1`, `DC Load2`, `DC Load3`

All four are Variable Resistor blocks, which is what makes load shedding free: commanding an open circuit is disconnecting the bay. No breaker, no extra state.

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| From Workspace × 4 | literal matrices, e.g. [0 5000; 0.2 5000; 0.25 12.8; 1 12.8] | mg.evLoad{1} … mg.evLoad{4} | Generated from session descriptions instead of typed. Arrival and departure stay sharp steps — two points 1 µs apart — because those are the interesting events. |
| Shed DC Load* (Switch) × 4 | — | new — R = shed_k ? mg.Rload_open : R_profile(t) | The shedding mechanism. |
| Open DC Load* (Constant) × 4 | — | new — mg.Rload_open = 1 MΩ | An open circuit. |
| From shed1 … From shed4 | — | new | The Supervisor's per-bay shed flags. Bay 4 sheds first, bay 1 last. |

## 4.11  `microgridLib.slx` — new library file

| Added | What it does |
| --- | --- |
| DC Droop Node | Inputs V0, Vbus; output Iref = sat(deadband(V0 − LPF(Vbus))/R, Imin, Imax). Mask: slope R, dead band DB, filter Tf, current limits, and filter initial value Vinit. Two linked instances in the model. |
| Droop Reference | Inputs V0, I; output Vref = sat(V0 − R·I). For a converter that already has its own voltage loop. Built but not instantiated — see → N14. |

### Change made to the library after it was first built

| Block / item | Before | After | Why |
| --- | --- | --- | --- |
| DC Droop Node/Meas filter | Transfer Fcn, [1]/[Tf 1] — no initial condition | a first-order lag built from an Integrator, IC = Vinit | A Transfer Fcn starts at zero, so both droop nodes computed Iref = (800 − 0)/R = 25 000 A and saturated at every start-up. → N8 |
| Mask parameters | 5 | 6 — Vinit added, set to mg.Vbus_nom on both instances | Propagates to every instance at once, which is the point of the library. |

# 5  Notes

The reasoning behind the changes in the tables above, including the attempts that failed first.

### N1  The legacy panel was producing zeros, not errors

41 unmatched From tags were not causing a hard error. The model has UnconnectedInputMsg set to warning, so Simulink was silently grounding every one of them and feeding zeros into the measurement maths. Everything that panel computed — bus power, DC power, PV power, battery power, RMS voltages, load P and Q — and the trace it fed to the master scope were meaningless numbers rather than obvious failures.

That is more dangerous than a compile error, and it is the reason the panel was taken out of the compile rather than left alone.

### N2  The transformer secondary — the fault that broke everything

With the new active front end in place, the DC link collapsed to zero in about five milliseconds, every time. Isolating the front end with the DC/DC gates forced off showed the link still collapsing with no load on it at all, which located the fault in the AC side rather than the control.

The secondary was grounded wye, and the DC bus negative rail is also grounded. A diode rectifier does not care. An IGBT bridge does: its common-mode voltage is a square wave at the scale of the DC link, and with both the AC neutral and the DC rail tied to the same ground there is a zero-sequence path straight through the winding. The transformer's zero-sequence reactance is only 0.03 pu.

Why Y and not Delta. Delta also blocks zero sequence, but introduces a 30° phase shift that the PLL and the voltage feed-forward would then have to account for. Ungrounded wye blocks the path and keeps the phase reference unchanged. The d–q control is unaffected by the floating neutral — the 2/3 Park transform rejects the common-mode component.

Effect: DC link went from collapsing to 0 V in 5 ms to holding 1600 V within ±4 V.

### N3  Why 1600 V on the DC link

A two-level voltage-source converter is a boost-type rectifier: its DC link must sit above the peak of the AC line-line voltage, √2 × 800 = 1131 V, or it degenerates into an uncontrolled diode bridge. With plain sinusoidal PWM the reachable phase peak is only half the link voltage, so 1131 V would leave no modulation margin at all. 1600 V gives a modulation index of about 0.82 at rated voltage — and makes the downstream DC/DC duty a convenient 800/1600 = 0.5.

### N4  The battery could not carry the park

The pack was fine while the grid was there to share the load. It did not survive the first islanding test, with all four bays charging and the battery as the only slack unit — about 192 kW on its own:

| Time | Bus | Battery current | Terminal voltage |
| --- | --- | --- | --- |
| 0.75 – 0.90 s | 783 V | 750 A | 236 → 231 V |
| 0.90 – 1.00 s | 783 → 648 V | 894 A, at the 900 A limit | 222 → 214 V |

Not depletion — the state of charge moved 0.016 % over the whole run. 192 kW from a 400 Ah pack is a 2.3C discharge against a block nominal discharge current of 124 A (0.31C). At that rate the terminal voltage collapses, and the droop law turns it into a runaway: less voltage means less power, so the bus sags, so the droop asks for more current, which sags it further. At 900 A the limiter saturated, the loop opened, and the bus fell to 648 V.

A current limit the plant cannot honour is not a limit, it is a cliff.

This was a sizing inconsistency present from the beginning: the dump resistor and the grid converter were both sized to the park rating, and the battery was the one unit sized below it. While the grid was there, nothing noticed. mg.Ibat_max is now derived from a power rating — 1.25 · Pbus_rated / Vbat_nom — so it cannot drift away from the pack again, and a regression check asserts the island duty stays under the block's own nominal discharge current.

To go back to the original pack, set mg.Vbat_nom and mg.Qbat_Ah and re-run build_05_battery_pack; the Battery block recomputes its discharge curve from those two numbers. Check 4.13 will then fail, correctly.

### N5  The PWM carrier convention

This one caused two failed attempts before it was found. The battery's PWM generator was an old instance whose triangular carrier runs 0 → 1, while every generator added during the grid rebuild uses −1 → +1. Same library block, same mask, different internal carrier. Feeding it m = 2D − 1 meant the modulating signal sat below the carrier permanently.

How it was found. Two sign hypotheses both produced the same wrong direction, which is impossible if the mapping were merely swapped. Forcing the duty open-loop to 0.15 and logging the pulses showed S1 duty = 1.000, S2 duty = 0.000 — not modulating at all. Reading the carrier definition inside the block explained why.

All three generators now share one convention, and a regression check compares them so they cannot diverge again.

### N6  A resistance that was load-bearing

The 1 Ω inductor resistance was the only thing limiting the battery current, and the current loop's gains — one unit of duty per amp — had effectively been tuned around it. Replacing it with a realistic 5 mΩ made the battery current run away to 3.8 kA: a plant correction breaking a controller. The gains were re-derived from the real inductor by internal model control at 1 kHz.

### N7  Bus capacitance is set by the droop design

The first droop run oscillated hard — bus 612 – 1065 V, both current references slamming into their limits. With proportional droop the loop bandwidth is not a free choice:

K  = 1/R_bat * D_bat_nom + 1/R_grid   ~ 30 A/V   (bus-side)

crossover = K / C_bus

At 4.7 mF, crossover landed at 1005 Hz — exactly on top of the converters' 1 kHz inner current loops. No cascade separation, so the bus rang. The droop band and the bus capacitance together fix the loop speed, so the fix is capacitance, not gain: 50 mF gives 625 rad/s, a 10× separation. For a 200 kW / 800 V bus that is 16 kJ, about 80 ms of ride-through — an ordinary figure for a DC microgrid.

The 4.7 mF was never a bus capacitor; it was the boost converter's own ripple capacitor, and the earlier sizing had taken it at face value.

A first attempt added a second capacitor in parallel. Its 1 mΩ series resistance made it an independent state with its own initial condition, and the two fought at t = 0 — the bus started at −500 V and took 50 ms to recover. Sizing the existing single capacitor avoids it entirely: one node, one state, the initial condition that already worked.

### N8  Measurement filters that start at zero

This appeared three times, in three different places, and is worth stating as a rule rather than as three isolated fixes.

| Where | Symptom |
| --- | --- |
| Voltage-Current Simscape Interface, v0 = 0 | At t = 0 the whole SPS network saw 0 V while every capacitor sat at 800 V — a 16 kA first-sample spike, and the droop controller's PI driven hard into its lower limit, from which it never recovered. |
| Subsystem1/LPF vq6, initialisation off | The droop set-point ramped from 0 to 800 V over the first 50 ms of every run. |
| DC Droop Node/Meas filter, a Transfer Fcn | A Transfer Fcn has no initial condition. Both droop nodes computed Iref = (800 − 0)/R = 25 000 A and saturated, slamming full current into a bus already at 800 V. This is where the start-up overshoot came from. |

A measurement filter that starts at zero tells the controller the plant is dead. In this model, any filter on a measurement gets an initial condition, and that initial condition is the operating point.

Fixing the third one brought the start-up peak from 819 V to 807.6 V, dropped the battery reference's first-5 ms peak from its limit to 117 A of 625 A, and let the checks reduce their start-up blind spot from 20 ms to 2 ms. What remains is not an overshoot: the bus starts at 800 V because that is where every capacitor is initialised, and relaxes to its droop equilibrium of about 794 V over 10 ms. Droop deliberately does not regulate to nominal, so that relaxation is correct.

### N9  Why the supervisor never touches a duty cycle

The Supervisor does exactly two things to each droop node: it moves the set-point V0, and it clamps the output current. Every command still reaches the plant through the droop law.

A supervisor that wrote duties directly would be a second, faster controller in parallel with the droop law, and the two would fight — exactly the failure mode droop exists to avoid.

Because it works through the droop law, the bus voltage remains the only communication path between converters and the decentralised structure survives intact. This is also why V0 was made an input rather than a mask parameter when the library block was built: that one decision is what made the entire SOC and islanding policy possible later without touching a single converter.

Why proportional, with no integrator. At steady state the bus settles at Vbus = V0 − R·Iref, and that slope is what shares load. An integrator would defeat it twice over: two integrating units in parallel each drive the bus to their own set-point and fight, and exact regulation destroys the sharing droop exists to provide. The bus is meant to sag under load.

### N10  Policy limits sit outside the droop node, not inside it

The library block's own current limits were deliberately left alone.

Those are the converter's physical rating — hardware. The Supervisor's limits are policy. Two limits of different kinds, in series, each visible on its own, and the library block stays reusable. Folding policy into the library mask would have meant every future instance carrying a supervisor-shaped hole in it.

Both limiters sit before the logging tap, so the recorded references are the ones the inner current loops actually received, not what the droop law asked for before the policy clipped it.

### N11  A tripped converter that was still eating the bus

Even with the pack correctly sized, the islanded bus dipped to 724 V for about 38 ms while the battery sat pinned at its limit — supplying 253 kW into a 178 kW load. Seventy-five kilowatts were going somewhere else:

| Time | DC link | Grid current (bus side) | DC/DC duty |
| --- | --- | --- | --- |
| 0.65 s (grid connected) | 1600 V | +194 A | 0.465 |
| 0.75 s | 1524 V | −28 A | 0.543 |
| 0.85 s | 1068 V | −35 A | 0.810 |
| 0.90 s | 802 V | −176 A | 0.939 |

Zeroing the grid droop node's current limits stopped the converter being commanded. It did not stop it switching. With the breaker open, the transformer secondary and the line reactor were still bolted to the bridge, so the front end went on modulating into them and pushed real current through their resistances — draining its own DC link capacitor from the inside. Once the link had decayed to the bus voltage, the downstream DC/DC could no longer hold the two apart and the bus discharged into the dead link.

The gate block is deliberately a protection, not a control action: it acts on the gates, not on a reference. A converter that may not be commanded must also not be able to act. It is what a real active front end does on loss of grid — it trips.

With the gates blocked the bridge is just its antiparallel diodes, the link holds its charge (1611 V, against 802 V before the fix), and because the link then stays well above the bus the DC/DC's own body diodes never forward-bias either.

### N12  Reconnection is three events, not one

| When | What happens |
| --- | --- |
| mg.t_island | The breaker opens. |
| mg.t_reconnect | The breaker closes. The grid is back on the transformer, but the converter is still gated off and its loops still hold whatever they wound up to while there was nothing to control. |
| + mg.t_resync | The gates are released. The PLL has had the window to lock, and the integrators — held in reset the whole time — start from zero rather than from their limits. |

Releasing the gates at the same instant the breaker closes would throw a wound-up converter at a live grid — which is how a real active front end trips.

This is why one flag became two. island answers is the breaker open; gridEnable answers may the converter act. They turn on and off at different times, and everything downstream already keyed off the right one, so the grid droop limits stay clamped through the resynchronisation window with no extra wiring.

Blocking the gates stopped the wound-up converter from mattering; it did not stop the winding up, which was acceptable only as long as nobody ever closed the breaker again. All three loops are stock Simulink PID blocks, so the reset needed no surgery — an external level reset holds each integrator at its initial condition for exactly as long as the gates are blocked.

### N13  Load shedding took three attempts

The rule it arrived at:

SHED below the droop band. RESTORE when the bus is back near nominal.

First attempt — ordinary hysteresis. Shed at 755 V, restore 25 V higher at 780 V. The overload scenario limit-cycled at 20 Hz: shed at 754 V, restored 24 ms later at 780 V, twelve times in half a second.

The reason is specific and worth keeping in mind: while the battery is pinned at its current limit the droop loop is open. The bus is no longer held by a controller, it is just the capacitor integrating the power imbalance. Dropping one 90 kW bay leaves about 113 A charging 50 mF, which takes the bus from 755 V through 780 V in 24 ms. Voltage hysteresis has no memory in time, and 24 ms is all the memory it had.

Second attempt — a slow restore signal. Shed on the instantaneous bus, restore only on a bus that has been healthy for 50 ms. The relays see max(−Vbus, −Vslow), and because they trip on the negated bus the maximum automatically picks whichever signal is more pessimistic in each direction. One filter and one comparison for all four stages — no timers, no latches, no state per bay. This cut the cycling from twelve changes to five, but did not stop it: with one bay shed the islanded bus settles at 782 V, genuinely above a 780 V restore point. The scheme was doing what it was told.

Third attempt — the thresholds were the real problem. Restore points now hang below nominal (790 / 785 / 780 / 775 V) rather than above the shed points. Referencing restore to the nominal bus states the real condition: put load back only when there is genuine headroom, not merely when the collapse has stopped getting worse. Setting restore just above the shed threshold looks like ordinary hysteresis and is not.

Result: one shed event, no chatter, islanded bus held at 782 V where it previously fell to 724 V.

### N14  Why the PV curtailment reference is fixed, not drooping

A droop slope for the PV was designed and left in the parameter file, giving Vref_pv = 850 − Rdroop_pv·Ipv. It is deliberately not used.

At rated PV current that reference droops to 850 − 20 = 830 V, which is below the mode relay's release point of 840 V. The PV would take over the bus, droop its own reference below the release threshold, get thrown back into MPPT, let the bus climb to 850 again — a limit cycle at the handover, caused entirely by the curtailment law fighting the mode selector.

A fixed set-point with latching hysteresis has neither problem. Once the PV has taken the bus it holds it at 850 V, which is the relay's own on-point, so the relay stays latched; it releases only when the bus actually falls to 840 V — that is, when the PV genuinely can no longer hold it. Droop on the PV reference would only be needed to share curtailment between multiple PV units, and there is one. mg.Rdroop_pv is kept, marked unused, for whoever adds the second array.

### N15  850 or 870: the two thresholds cannot both be 850

The specification suggested "for example 850 V" for the dump resistor and "maybe around 850 V" for the PV voltage-control mode.

The dump resistor has to sit above the PV curtailment threshold, or the resistor fires first and the park burns energy it could simply have stopped generating. So the PV curtails at 850 V and the dump resistor fires at 870 V. Both are single lines in the parameter file.

The ordering works in practice: in the curtailment scenario the bus peaks at 855 V and the resistor never fires. It has become what it should be — a backstop that never operates, because the PV backs off 15 V before it.

### N16  Zero-crossing chatter, and one solver setting

Late in the work, adding filters to the Supervisor changed the model's continuous state vector, which changed the variable-step solver's step selection, which pushed the PV boost's ideal switching IGBT into zero-crossing chatter. The simulation aborted at 7.6 ms with 1000 consecutive zero-crossing events.

This is a numerical fragility of ideal switches under a variable-step solver, not a control fault — nothing about the circuit or the controllers had changed, and the failure was triggered by adding signal-path blocks the PV boost never sees. ZeroCrossAlgorithm = Adaptive is what Simulink provides for exactly this case: it relaxes the crossing tolerance when a signal chatters instead of aborting. The start-up is identical either way.

Worth carrying forward: an ideal switching device plus a variable-step solver means unrelated additions can break a run. A regression check pins the setting so it cannot quietly revert.

# 6  Verification

All figures from the model as delivered, re-run from a cold start.

## 6.1  Structural checks — 64 / 64 pass

| Area | Checks | Covers |
| --- | --- | --- |
| Model integrity | 11 | parameter loading, unresolved tags, unconnected ports, scope channels, dashboard bindings, powergui and solver settings |
| Grid path and plant | 13 | bridge device and gating, transformer connection, converter blocks, drain hysteresis and sizing, battery passives, interface and filter initialisation |
| Converter loops | 8 | complementary switching, duty feed-forward, PWM carrier convention, anti-windup, export limits, PV reference |
| Droop layer | 7 | library links, slopes, limits, filter time constant, set-points as signals, bus capacitance |
| Supervisor | 13 | published signals, algebraic-loop-free filtering, set-point sources, policy limiters, hysteretic thresholds, gate blocking, pack rating |
| Islanding, shedding, sessions | 12 | filter initialisation, island window, resync ordering, breaker cycle, integrator resets, shed staging and restore lag, generated profiles, solver setting |

## 6.2  Supervisor threshold sweep — 15 / 15 pass, in 4 seconds

| Check | Result |
| --- | --- |
| Discharge blocked below the SOC target | limit = 0 A |
| Discharge released above it | limit = 625 A |
| Charging blocked at a full pack | limit = 0 A while held at 100 % |
| Set-point bias against the clamped law | max deviation 0.000 V over 790.0 – 804.0 V |
| Discharge-limit hysteresis | opens at 81.06 %, closes at 78.96 % (designed 81.0 / 79.0) |
| Threshold chattering | 2 transitions each over a 0→100→0 sweep — the minimum possible |
| PV handover | MPPT below 840 V, voltage control above 850 V |
| Shed stages 1 – 4 | each fires below its own threshold; all four confirmed |
| Restoration | no bay still shed once the bus is back at 860 V |

## 6.3  Full simulation — 36 / 36 pass

One second; four bays arriving in sequence; grid out at 0.70 s, breaker back at 0.82 s, converter released at 0.87 s.

| Measure | Result |
| --- | --- |
| Bus over the whole run | 764 – 799 V |
| Start-up peak | 807.6 V, references never near their limits |
| Islanding transient | 784 – 788 V — a 5 V dip |
| Resynchronisation window | grid reference exactly 0 A between reclose and release |
| Gate release transient | 778 – 788 V |
| Reconnected, settled | 786 – 793 V, grid reference +161 A |
| Battery hand-back | +402 A islanded → −18 A reconnected |
| DC link | 1597 V grid-connected, 1599 V after reconnection |
| Battery current | peak 403 A against a 625 A limit |
| Battery current tracking | 3.0 A rms on a 403 A span |
| Dump resistor | never fired (peak 799 V against a 870 V threshold) |
| Load shedding | never fired |
| Below-target discharge block | limit = 0 A across all 22 062 grid-connected samples |
| Grid covers the deficit | mean grid reference +126 A (import) |

## 6.4  Scenarios

| Scenario | Tests | Result |
| --- | --- | --- |
| soc90 | "except when the battery is above 80 % SOC" | 5 / 5. Discharge limit released to 625 A; set-point biased to 802.0 V against the grid's 800.0 V; battery +85 A discharging; battery 34 kW vs grid 12 kW; bus 797 – 802 V. |
| pvcurtail | "if the battery is full and the loads are provided, the PV switches to voltage control" | 6 / 6. Charge limit 0 A; voltage control active 76 % of the run; handover at 852 V; bus held at 853 V; peak 855 V, never reaching the 870 V dump resistor; one mode transition. |
| overload | 360 kW demanded of a 250 kW pack | 6 / 6. One of four bays dropped at 754 V; one stage change over the run; islanded bus low point 782 V; battery 550 A against a 625 A limit; grid-connected operation untouched. |

## 6.5  Checks narrowed as the design advanced

Where later work legitimately superseded an earlier acceptance criterion, the check was narrowed rather than deleted, so the surviving structure stayed covered.

| Check | Was | Now |
| --- | --- | --- |
| Grid inner loop | the inner PI plus a droop gain and the outer PID limits | the inner current PI only — the rest moved into the droop node |
| Battery loops | both battery PI blocks | the current loop only — the outer PI became a droop node |
| Export limit | on the outer PID | on the grid droop node |
| Dashboard bindings | irradiance knob and the manual PV mode switch | irradiance knob only — the manual switch was removed on purpose |
| Breaker | SwitchTimes is exactly the islanding time | the islanding time is what opens it; a separate check owns the full cycle |